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Four Lakes Water District #10
2025 Water Use Efficiency Report

WATER USE EFFICIENCY RULE
The Washington State Department of Health (DOH) requires all public water systems to comply with the Water Use Efficiency (WUE) Rule adopted in 2007 under the Municipal Water Law. This rule requires systems to establish supply-side and demand-side goals and report annually to customers on progress toward achieving those goals.
 Four Lakes Water District #10 provides a summary of adopted WUE goals, measures, and progress using the water systems reporting format.
WATER USE EFFICIENCY GOALS AND MEASURES
Supply Side Goal
Maintain distribution system leakage below 10% annually.
Measures to Achieve Goal
· Conduct annual and monthly water loss audits
· Locate and repair leaks in a timely manner
· Perform leak detection in distribution and transmission mains as needed
· Prevent reservoir overflows
· Continue meter replacement and accuracy improvements
Demand Side Goal
Reduce average annual consumption per residential connection by 1% over a six-year period.
Measures to Achieve Goal
· Provide annual conservation education to customers
· Include conservation messaging on monthly utility bills
· Maintain inclining rate structure to incentivize reduced use
· Promote rebate programs for efficient fixtures and appliances
· Provide consumption history on water bills to encourage awareness
SUMMARY OF PROGRESS
The Four Lakes system demonstrates continued progress in water conservation and system efficiency:
To better evaluate demand-side conservation progress, the district tracks total customer water use both including seasonal irrigation demand and excluding estimated irrigation use. This distinction helps show how baseline residential consumption compares with higher summer demand driven by outdoor watering.
	Demand-Side Measure


	2024 Water Use
	2025 Water Use
	Progress Note

	Total customer water use, including irrigation
	20,776,000 gallons
	20,995,000 gallons
	Total use reflects all metered customer demand, including seasonal outdoor irrigation.

	Customer water use, excluding irrigation
	8,276,580 gallons

	7,880,000 gallons

	Non-irrigation use provides a clearer measure of indoor and baseline residential conservation progress.


·  Historical graph showing water use from the same period last year to help customers compare current usage trends with prior-year demand
· Ongoing leak detection and repair efforts have maintained leakage rates generally below the 10% DOH threshold
· Meter replacement programs have improved system accuracy and reduced apparent losses
· Public education continues through brochures, billing messages, and direct outreach to customers
· Irrigation restrictions (June–September, no watering 10 a.m.–7 p.m.) remain in effect to reduce evaporative loss
Operational improvements and capital investments (including new transmission infrastructure and well utilization projects) are expected to further enhance system reliability and efficiency.


2025 WATER USE STATISTICS
Reporting Period: 2024 – 2025 
· Total Water Produced & Purchased: 20,767,000 gallons
· Authorized Consumption: 20,245,000 gallons
· Unaccounted Water: 531,000 gallons
· Distribution System Leakage (DSL): 2.6%
Assessment: System leakage remains below the 10% state performance standard and is within the district goal.

HISTORICAL LEAKAGE PERFORMANCE
Recent distribution system leakage rates:
· 2022–2023: 9.72%
· 2023–2024: 6.32%
· 2024-2025: 2.6%
Variations in leakage were influenced by system leaks and emergency events such as wildfire response demands (Gray Road Fire, August 2023).

CUSTOMER USE TRENDS
The district continues to track customer consumption and promote conservation behavior through billing transparency and education. Based on the demand-side goal data, Four Lakes used 20,776,000 gallons in 2024 and 20,995,000 gallons in 2025. Historical data shows variability in annual usage driven by seasonal demand and system events, with ongoing efforts to reduce per-connection consumption over time.

CONTINUED CONSERVATION EFFORTS
The water district will continue to implement and expand the following efforts across the Four Lakes system:
· Leak detection and infrastructure replacement
· Meter modernization and data collection improvements
· Public outreach and conservation education
· Water-efficient rebate programs
· Enforcement of seasonal irrigation restrictions
These programs align with the water systems' broader water conservation strategy and long-term system planning.

CONTACT INFORMATION
For questions regarding this report or water conservation programs, please contact:
FOUR LAKES WATER DISTRICT
Phone: (509) 299 7333
Four Lakes WA 99014-0047

This report is provided annually to comply with Washington State Water Use Efficiency Rule requirements.
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